# Maintenance Schedule for Cooling Towers

| Description | Comments | Maintenance Frequency |
| --- | --- | --- |
| Cooling tower use/ sequencing | Turn on/sequence unnecessary cooling towers | Daily |
| Overall visual inspection | Complete overall visual inspection to be sure all equipment is operating and safety systems are in place | Daily |
| Fan motor condition | Check the condition of the fan motor through temperature or vibration analysis and compare to baseline values | Weekly |
| Clean suction screen | Physically clean screen of all debris | Weekly |
| Operate make-up water float switch | Operate switch manually to ensure proper operation | Weekly |
| Vibration | Check for excessive vibration in motors, fans, and pumps | Weekly |
| Check tower structure | Check for loose fill, connections, leaks, etc. | Weekly |
| Check belts and pulleys | Adjust all belts and pulleys | Weekly |
| Test water samples | Test for proper concentrations of dissolved solids, and chemistry. Adjust blowdown and chemicals as necessary. Perform weekly for open towers and monthly for closed systems. | Weekly (Open) Monthly (Closed) |
| Check lubrication | Assure that all bearings are lubricated per the manufacture's recommendation | Monthly |
| Check motor supports and fan blades | Check for excessive wear and secure fastening | Monthly |
| Motor alignment | Aligning the motor coupling allows for efficient torque transfer | Monthly |
| Check drift eliminators, louvers, and fill | Look for proper positioning and scale build up | Monthly |
| Inspect nozzles for clogging | Make sure water is flowing through nozzles in the hot well | Annually |
| Clean tower | Remove all dust, scale, and algae from tower basin, fill, and spray nozzles | Annually |
| Check bearings | Inspect bearings and drive belts for wear. Adjust, repair, or replace as necessary. | Annually |
| Motor condition | Checking the condition of the motor through temperature or vibration analysis assures long life | Annually |