# Maintenance Schedule for Water Distribution Systems

| Description | Comments | Maintenance Frequency |
| --- | --- | --- |
| Check pump use/sequencing | Turn off/sequence unnecessary pumps. | Daily |
| Visually inspect pumps, valves, and all mechanical joints | Visually inspect components to ensure that all equipment is operating, safety systems are in place, and no unusual leaks exist. | Weekly |
| Test water | Test for proper concentrations of dissolved solids and chemistry. Adjust chemicals as necessary. | Monthly |
| Check lubrication | Ensure that all bearings are lubricated according to manufacturer’s recommendations. | Monthly |
| Check packing | Check packing for wear and repack as necessary. Consider replacing packing with mechanical seals. | Monthly |
| Check mechanical seals | Check for leakage that exceeds the manufacturer’s specifications. Replace if necessary. | Monthly |
| Motor/pump alignment | Align the pump/motor coupling to ensure efficient torque transfer to the pump. | Annually |
| Check mountings | Check and secure all pump mountings. | Annually |
| Check bearings | Inspect bearings and drive belts for wear. Adjust, repair, or replace as necessary. | Annually |
| Check strainers | Clean strainers. | Annually |
| Check expansion tanks | Inspect these tanks to make sure that the acceptance capacity is adequate and that they function properly. | Annually |
| Inspect heating and cooling heat exchangers. | Temperature differences may indicate air binding, clogged strainers, or excessive scale. Determine the cause and correct. | Annually |
| Cycle valves | Observe the valves moving through their full range from closed to 100% open. Back off one-half turn from 100% open to prevent the valve from “freezing” in the full open position. | Annually |
| Motor condition | Check the condition of the motor through temperature or vibration analysis. | Annually |